## Sheet1
Annex D List of Requirements for Annual Periodic Inspection
ITEM | REQUIREMENT | Requirements Applicable to the relevant version of I.S. 3217.
|  | 1989 | 2008 | 2013
a | Mode of operation for emergency exit signs is maintained (2) | Yes | Yes | Yes
b | There is evidence that the system is being adequately maintained | Yes | Yes | Yes
c | Emergency exit signs clearly and unambiguously indicate direction of escape | Yes | Yes | Yes
d | All emergency luminaires and signs are operational and meet the full durational test requirements | Yes | Yes | Yes
e | Following the completion of the full duration test all emergency lighting indicators show healthy status | Yes | Yes | Yes
f | The following points of emphasis have emergency luminaire(s) (4)
| 1) each staircase | Yes | Yes | Yes
| 2) each change in floor level | Yes | Yes | Yes
| 3) each change of direction | Yes | Yes | Yes
| 4) each fire alarm call point | Yes | Yes | Yes
| 5) fire fighting equipment | Yes | Yes | Yes
| 6) each emergency exit door | Yes | Yes | Yes
| 7.1) Outside each final exit and outside the building to a place of safety | N/A | N/A | Yes
| 7.2) Outside each final exit and close to it (1) | Yes | Yes | N/A
| 8) emergency exit and safety signs required by the enforcing authority | Yes | Yes | Yes
| 9) each first aid post | N/A | Yes | Yes
| 10) each intersection of corridors | Yes | Yes | Yes
| 11) Near escape equipment provided for the disabled | N/A | Yes | Yes
g | The following locations have emergency escape lighting provided
| 1) Lift cars | Yes | Yes | Yes
| 2) Moving stairways and walkways | Yes | Yes | Yes
| 3) Toilets and toilet lobbies | Yes | Yes | Yes
| 4) Disabled toilets | Yes | Yes | Yes
| 5) Refuge areas for the mobility impaired | N/A | Yes | Yes
| 7) Motor generator, control, switch and plant rooms | Yes | Yes | Yes
| 7) Covered car parks (pedestrian escape routes) | Yes | Yes | Yes
| 8) Open areas greater than 60m2 | N/A | Yes | Yes
| 9) High risk task areas | N/A | Yes | Yes
h | There is a suitable test facility for simulating failure of supply | Yes | Yes | Yes
i | In the event of circuit failures on emergency escape stairwells, emergency escape lighting is present and functions (3) | Yes | Yes | Yes
j | It is the opinion of the persons(s) undertaking the Annual Inspection & Testing that the illuminance requirements of the applicable version(s) of I.S. 3217 are complied with and that emergency lighting is provided in all locations as required by the applicable version(s) of I.S. 3217. | Yes | Yes | Yes
(1)3217 1989 - may rely on local authority lighting if adequate
(2) I.S.3217 1989 - Please refer to Annex F of this standard for exceptions: In particular F2, F3, F4, F6, F8.2.
(3) ensure that suitable measures and (1) I.S. precautions are taken to safeguard the building occupants.
(4) For specific requirements of items listed in “f “, please refer to the applicable standards.